CMP12系列太阳能充放电控制器使用说明书

CMP12太阳能充放电控制器系我公司自主开发的最新专利产品，适合12V（120瓦太阳能板）或24V（240瓦太阳能板）太阳能发电系统的自动控制。

I功能：

1.过载保护	2.短路保护	3.雷电保护	4欠压保护	5.过充保护

II 接线：

揭开控制器上盖，露出接线端子，按上盖图示连接：

1．将蓄电池的“+”、“-”极正确牢固地连接到控制器相应的端子上(左起第3、第4)。

*负荷指示灯（load）闪动一下后会亮起，表示连接正确，可继续进行下列连接。否则会损坏控制器。

2．将太阳能板的“+”、“-”极正确牢固地连接到控制器相应的端子上(左起第1、第2)。

*如果连接错误会损坏你的控制器。

3．将负载的“+”、“-”极正确牢固地连接到控制器相应的端子上（左起第5、第6）

III 指示灯：

1．充电指示灯1支（charge），亮起表示正在强力充电，闪动表示正在浮动充电，不亮表示充电已经停止。

2．负荷指示灯1支（load），亮起表示有输出，负载可以工作；不亮表示没有输出，负载不能工作。

注意事项：

1．接线前请仔细核对并确认太阳能板、蓄电池、负载的额定电压，三者的额定电压应相同，且都是12V或者都是24V。

2．太阳能板、负载的额定电流不得大于控制器的额定电流。

附参数表：

| 额定电压 | 6V,12V或24V | 供电停止电压 | 5.4V,10.8V/21.6V |
| --- | --- | --- | --- |
| 额定充电电流 | 5A 10A 15A 20A | 供电恢复电压 | 6.3V,12.6V /25.2V |
| 额定负载电流 | 5A 10A 15A 20A | 充电停止电压 | 7.2V,14.4V /28.8V |
| 工作温度 | -20 ~ +60℃ | 停充电压温度系数 | -3mV/℃/cell |
| 外形尺寸(L*W*H) | 103×95×38 mm | 净重 | 120g～ 160g |

*参数可根据用户要求定制。

# CMP12 SOLAR CHARGE CONTROLLER

# User’s manual

# The product is used to control Solar Panel and battery in Solar System automatically. Here is the Solar Panel Configuration list with different rated voltage (12V and 24V).

Ⅰ. FUCTION:

1. Over-load protection

2. Short circuit protection

3. Lightning protection

4. Under-voltage protection

5. Over-charging protection

Ⅱ. CONNECTION (AS INDICATED IN DIAGRAM):

Open the top cover of controller and connect the wire with terminals follow the diagram on the top cover of it.

1. Connect the “+”, “-” Poles of the battery to the corresponding ports of controller (the third and the fourth one from left).

* The subsequent operation can be processed if only if load indicator (mark: load) flickers once and starts lighting. Otherwise, the subsequent operation will damage the controller.

2. Connect the “+”, “-” poles of the solar panel to the corresponding ports of controller (the first and the second one from left).

* If a connection error can damage your controller.

3. Connect the “+”, “-” poles of the load to the corresponding ports of controller (the fifth and the sixth one from left).

Ⅲ. INDICATOR LED

1. Charge LED is used to indicate the charging status of battery. Lighting is in-charging mode, flashing is floating charge mode. LED turn off means charging stopped.

2. There is output and load can work if the Load LED is lighting. There isn’t output and the load cannot work if Load LED off.

# Notice:

1. Please make sure the rated voltage of solar panels, batteries the loads are the same. All of them should be 6V, 12V or 24V.

2. The rated current of solar panels and load must be less than the rated current of controller.

# The specifications:

| Rated voltage | 6V,12V/24V | Voltage of stop power supply | 5.4V,10.8V/21.6V |
| --- | --- | --- | --- |
| Rated charging current | 5A 10A 15A 20A | Voltage of resume power supply | 6.3V,12.6V /25.2V |
| Rated load current | 5A 10A 15A 20A | Voltage of stop charging | 7.2V,14.4V /28.8V |
| Working temperature | -20 ～ +60℃ | Temperature coefficient of voltage stop charge | -3mV/℃/cell |
| Dimension(L*W*H) | 103×95×38mm | Net weight | 120g～ 160g |

Parameters may customized by customers.